欧规(IEC标准)与美规(UL标准)保险管熔断时间表:

一. 快熔断

美规(UL标准)..

ELECTRICAL CHARACTERISTICS:

| Inf or If | 110% of In | 135% of In | 200% of In |
| --- | --- | --- | --- |
| In | Min. | Max. | Max. |
| 50mA – 6.3A | 4 hrs | 60min | 2min |

In = Rated Current, If = Fusing Current, Inf = Non-Fusing Current

Pre-arcing time/current characteristics at Ta = 23 C

欧规(IEC标准)

ELECTRICAL CHARACTERISTICS:

| Inf or If | 150% of In | 210% of In | 275% of In |  | 400% of In |  | 1000% of In |
| --- | --- | --- | --- | --- | --- | --- | --- |
| In | Min. | Max. | Min. | Max. | Min. | Max. | Max. |
| 32mA – 100mA | 60min | 30min | 10ms | 500ms | 3ms | 100ms | 20ms |
| 125mA – 10A | 60min | 30min | 50ms | 2s | 10ms | 300ms | 20ms |

In = Rated Current, If = Fusing Current, Inf = Non-Fusing Current

Pre-arcing time/current characteristics at Ta = 23 C

二.慢熔断

美规(UL标准)

ELECTRICAL CHARACTERISTICS:

| Inf or If | 110% of In | 135% of In | 200% of In |  |
| --- | --- | --- | --- | --- |
| In | Min. | Max. | Max. | Min |
| 80mA - 3A | 4 hrs | 60min | 120s | 5s |
| 3.15A – 10A | 4 hrs | 60min | 120s | 12s |

In = Rated Current, If = Fusing Current, Inf = Non-Fusing Current

Pre-arcing time/current characteristics at Ta = 23 C

欧规(IEC标准)

ELECTRICAL CHARACTERISTICS:

| Inf or If | 150% of In | 210% of In | 275% of In |  | 400% of In |  | 1000% of In |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| In | Min. | Max. | Min. | Max. | Min. | Max. | Min. | Max. |
| 50mA – 100mA | 60min | 2min | 200ms | 10s | 40ms | 3s | 10ms | 300ms |
| 125mA – 20A | 60min | 2min | 600ms | 10s | 150ms | 3s | 20ms | 300ms |

In = Rated Current, If = Fusing Current, Inf = Non-Fusing Current

Pre-arcing time/current characteristics at Ta = 23 C