Harmonics – Class-C per A-14(Run time)

EUT: Equipment under test	Tested by: Tested by

Test category: Class-C per A-14 (European limits)	Test Margin: 100

Test date: 2000-1-1	Start time: 0:09:15	End time: 0:10:25

Test duration (min): 1	Data file name: H-000181.cts_data

Comment: Comment

Customer: Customer information

Test Result: Pass	Source qualification: Normal

Current & voltage waveforms

Harmonics and Class C limit line (Table-3 Class-D)	European Limits

Test result:  Pass     or waveform fails phase angle spec. - see below

Current Test Result Summary (Run time)

EUT: Equipment under test	Tested by: Tested by

Test category: Class-C per A-14 (European limits)	Test Margin: 100

Test date: 2000-1-1	Start time: 0:09:15	End time: 0:10:25

Test duration (min): 1	Data file name: H-000181.cts_data

Comment:  Comment

Customer:  Customer information

Test Result: Pass	Source qualification:  Normal

THC(A): 0.01       I-THD(pk%): 5.96         POHC(A):  0.001        POHC Limit(A):  0.010

Highest parameter values during test:

V_RMS (Volts): 	120.09	Frequency(Hz):   60.00

I_Peak (Amps):	0.299	I_RMS (Amps):	0.196

I_Fund (Amps):	0.195	Crest Factor:	1.539

Power (Watts): 	23	Power Factor:	0.997

Harm#	Harms(avg)	100%Limit	%of Limit	Harms(max)	150%Limit	%of Limit	Status

2	0.000

3	0.011	0.080	13.5	0.011	0.120	9.28	Pass

4	0.000

5	0.002	0.045	5.3	0.003	0.067	4.29	Pass

6	0.000

7	0.001	0.023	3.3	0.001	0.035	2.69	Pass

8	0.000

9	0.000	0.012	3.5	0.001	0.018	3.64	Pass

10	0.000

11	0.000	0.008	5.9	0.001	0.012	6.14	Pass

12	0.000

13	0.000	0.007	6.0	0.001	0.010	6.87	Pass

14	0.000

15	0.000	0.006	5.8	0.001	0.009	6.63	Pass

16	0.000

17	0.000	0.005	6.5	0.001	0.008	6.63	Pass

18	0.000

19	0.000	0.005	6.9	0.001	0.007	7.66	Pass

20	0.000

21	0.000	0.004	7.9	0.001	0.006	7.88	Pass

22	0.000

23	0.000	0.004	7.9	0.000	0.006	7.68	Pass

24	0.000

25	0.000	0.004	9.3	0.000	0.005	9.14	Pass

26	0.000

27	0.000	0.003	12.6	0.001	0.005	10.63	Pass

28	0.000

29	0.000	0.003	13.8	0.001	0.005	11.60	Pass

30	0.000

31	0.000	0.003	15.0	0.001	0.004	12.42	Pass

32	0.000

33	0.000	0.003	14.7	0.001	0.004	12.42	Pass

34	0.000

35	0.000	0.003	15.6	0.000	0.004	12.79	Pass

36	0.000

37	0.000	0.002	19.5	0.001	0.004	18.78	Pass

38	0.001

39	0.001	0.002	22.0	0.001	0.003	16.98	Pass

40	0.000

Note: Dynamic limits were applied for this test (Class C < 25 Watts).

Voltage Source Verification Data (Run time)

EUT: Equipment under test	Tested by: Tested by

Test category: Class-C per A-14 (European limits)	Test Margin: 100

Test date: 2000-1-1	Start time: 0:09:15	End time: 0:10:25

Test duration (min): 1	Data file name: H-000181.cts_data

Comment:  Comment

Customer:  Customer information

Test Result: Pass	Source qualification: Normal

Highest parameter values during test:

Voltage (Vrms): 	120.09	Frequency(Hz):   60.00

I_Peak (Amps):	0.299	I_RMS (Amps):	0.196

I_Fund (Amps):	0.195	Crest Factor:	1.539

Power (Watts): 	23	Power Factor:	0.997

Harm#	Harmonics V-rms	Limit V-rms	% of Limit	Status

2	0.172	0.240	71.61	OK

3	0.312	1.081	28.89	OK

4	0.013	0.240	5.46	OK

5	0.055	0.480	11.42	OK

6	0.007	0.240	2.92	OK

7	0.014	0.360	3.90	OK

8	0.009	0.240	3.59	OK

9	0.016	0.240	6.46	OK

10	0.022	0.240	9.06	OK

11	0.010	0.120	8.12	OK

12	0.005	0.120	3.76	OK

13	0.007	0.120	5.57	OK

14	0.006	0.120	4.93	OK

15	0.011	0.120	8.91	OK

16	0.008	0.120	6.44	OK

17	0.005	0.120	3.93	OK

18	0.007	0.120	6.03	OK

19	0.003	0.120	2.58	OK

20	0.009	0.120	7.39	OK

21	0.004	0.120	3.48	OK

22	0.005	0.120	4.07	OK

23	0.003	0.120	2.24	OK

24	0.003	0.120	2.31	OK

25	0.005	0.120	4.47	OK

26	0.005	0.120	3.82	OK

27	0.003	0.120	2.63	OK

28	0.003	0.120	2.58	OK

29	0.004	0.120	3.20	OK

30	0.004	0.120	3.12	OK

31	0.002	0.120	2.02	OK

32	0.003	0.120	2.26	OK

33	0.004	0.120	3.53	OK

34	0.002	0.120	1.29	OK

35	0.002	0.120	2.06	OK

36	0.002	0.120	1.64	OK

37	0.003	0.120	2.50	OK

38	0.003	0.120	2.82	OK

39	0.002	0.120	2.08	OK

40	0.003	0.120	2.09	OK