UNDERWRITERS LABORATORIES INC.			     APPLIANCE WIRING MATERIAL
Subj. 758		Section 2		Page 20276       Issued:  1983-08-16
								    Revised:  2003-06-05

Style 20276		Electronic Cable.
______________________________________________________________________________

Rating		60C or 80C, 30 V.
______________________________________________________________________________

Insulated		No. 40 AWG minimum.  Labeled or complying with AWM
Conductors		Procedure having a minimum rating of 60C or 80C 
			whichever is applicable.
______________________________________________________________________________

Assembly		Consists of two or more conductors, twisted pairs, 
			parallel pairs, or groups of twisted conductors or 
			parallel pairs twisted together.  The conductors or 
			groups of conductors may be laid parallel forming a flat, 
			oval or round cable.  The lay of the insulated conductors 
			are not specified.  A barrier layer and/or fillers are 
			optional.  Manufacturer shall maintain a complete 
			description of each assembly.  May use same or mixed AWG 
			size.
______________________________________________________________________________

Covering		(Optional.)  A 6 mil or heavier PVC covering may be 
			extruded over the conductor assembly.
______________________________________________________________________________

Shield		Optional.
______________________________________________________________________________

Jacket		PVC, Class 43.

			    Thickness (mils)
		          Construction A	    Construction B
			    External Use		    Internal Use

			#Dia. under		            Minimum		    Minimum
			 jacket in	       Minimum	  at       Minimum      at
			  inches__		 Average   any Point   Average   any Point

			0.350 or less	    20        17         15         12
			0.351 - 0.700	    30        24         30         24
			0.701 - 1.00	    40        36         40         36
			0.101 - 1.50	    54        48         54         48
______________________________________________________________________________

Standard		Appliance Wiring Material UL 758.
______________________________________________________________________________
								(Continued on Page 20276A)

UNDERWRITERS LABORATORIES INC.	         	     APPLIANCE WIRING MATERIAL
Subj. 758 		Section 2		Page 20276A	     Issued:  1983-08-16
								    Revised:  2003-06-05

Instructions	Detailed Examination.
to UL			Physical Properties of Jacket.
Representative	
			The designation of all Styles of the individual 
conductors used making up the cable assembly shall be 
available, and the UL Representative's tag shall indicate 
if the Style is labeled or not.  If they are not labeled, 
the appropriate Follow-Up Tests shall be conducted.
______________________________________________________________________________

UL			(4)  Detailed Examination.
*Counter-Check	(4)  Physical Properties of Jacket.
*Program		(4)  Heat Shock.
*			(4)  Cold Bend.
*			(4)  Deformation.
			(12) Cable Flame Test on Completed Cable, 
			     Construction A only. 
			(12) Horizontal Flame Test on Completed Cable, 
			     Construction B only.

			If the insulated Styles are not labeled, the appropriate 
			Follow-Up Tests shall be conducted.
______________________________________________________________________________

Marking		General.
______________________________________________________________________________

Use			Construction A:  Internal wiring or external 
			interconnection of electronic equipment in Class 2 
			circuits only.

			Construction B:  Internal wiring of electronic equipment 
			in Class 2 circuits only.