## Power Supply 115V
Manufacturer:
SKU Number: |  |  | Cord Length (cm):
Product Description: |  | 12V 5A
Enter Applicable Nameplate Information
Rated AC Input Voltage |  | 115 | VAC
Rated Input Power |  | 60 | W
Rated AC Input Current |  |  | A
Rated Input Volt-Amperes |  |  | VA
Rated Input AC Frequency |  | 60 | Hz
Rated Output Voltage |  | 12 | V
Rated Output Current |  | 5000 | mA
Efficiency Level Mark
Energy Star Qualified?
Manufactured Date
Comments:
Tier 1 Standards
Minimum Average Efficiency in Active Mode:
< 1 Watt |  | 0.49 * Nameplate Output
≥ 1 to ≤ 49 Watts |  | 0.09 * Ln ( Nameplate Output ) + 0.49
> 49 Watts |  | 0.84
Maximum Energy Consumption in No Load Mode:
0 to < 10 Watts |  | 0.5 W
≥ 10 to ≤ 250 Watts |  | 0.75 W
Test Method: | EPA Test Method for Calculating the Energy Efficiency of Single-Voltage
External Ac-Dc and Ac-Ac Power Supplies - August 11, 2004
CEC Effective Date: |  | Manufactured On or After 7/1/2006
Tier 1 Standards for This Power Supply
Rated Output Power (Voltage x Current): |  |  | 60 | W
Maximum Energy Consumption - No Load: |  |  | 0.75 | W
Minimum Average Efficiency in Active Mode: |  |  | 0.84 | 84%
115 VAC / 60 Hz External Power Supply Results Summary
|  | Sample #1 | Sample #2 | Sample #3 | Average
100% Load Efficiency |  | 81.27% |  |  | 81.27%
75% Load Efficiency |  | 83.3% |  |  | 83.3%
50% Load Efficiency |  | 84.93% |  |  | 84.93%
25% Load Efficiency |  | 83.22% |  |  | 83.22%
Average Active Mode Efficiency |  | 83.18% |  |  | 83.18%
No Load Input Power (W) |  | 0.6 |  |  | 0.6
Enter Nameplate Information and Sample #1, #2, #3 Data
Test Lab: |  |  |  | Date: | 2006-09-14
Technician: |  |  |  |  | 1.0

## Sample #1
Sample #1 Test Results - 115 VAC / 60 Hz
Output Measurements |  |  | AC Input Measurements
Load Condition #1: 100%
Set Output Current to | 5000 | mA | Measured Input Power | 74.2 | W
Min Output Current | 4900 | mA | Measured Input Voltage | 115 | VAC
Max Output Current | 5100 | mA | Measured Frequency | 60 | Hz
True Power Factor
Measured Output Current | 5000 | mA | Total Harmonic Distortion (THD) |  | %
Measured Output Voltage | 12.06 | V | Calculated Power Consumed | 13.9 | W
Calculated Output Power | 60.3 | W | Calculated Efficiency (Ouput/Input) | 81.27%
Load Condition #2: 75%
Set Output Current to | 3750 | mA | Measured Input Power | 54.2 | W
Min Output Current | 3650 | mA | Measured Input Voltage | 115 | VAC
Max Output Current | 3850 | mA | Measured Frequency | 60 | Hz
True Power Factor
Measured Output Current | 3750 | mA | Total Harmonic Distortion (THD) |  | %
Measured Output Voltage | 12.04 | V | Calculated Power Consumed | 9.05 | W
Calculated Output Power | 45.15 | W | Calculated Efficiency (Ouput/Input) | 83.3%
Load Condition #3: 50%
Set Output Current to | 2500 | mA | Measured Input Power | 35.5 | W
Min Output Current | 2400 | mA | Measured Input Voltage | 115 | VAC
Max Output Current | 2600 | mA | Measured Frequency | 60 | Hz
True Power Factor
Measured Output Current | 2500 | mA | Total Harmonic Distortion (THD) |  | %
Measured Output Voltage | 12.06 | V | Calculated Power Consumed | 5.35 | W
Calculated Output Power | 30.15 | W | Calculated Efficiency (Ouput/Input) | 84.93%
Load Condition #4: 25%
Set Output Current to | 1250 | mA | Measured Input Power | 18.1 | W
Min Output Current | 1150 | mA | Measured Input Voltage | 115 | VAC
Max Output Current | 1350 | mA | Measured Frequency | 60 | Hz
True Power Factor
Measured Output Current | 1250 | mA | Total Harmonic Distortion (THD) |  | %
Measured Output Voltage | 12.05 | V | Calculated Power Consumed | 3.0375 | W
Calculated Output Power | 15.0625 | W | Calculated Efficiency (Ouput/Input) | 83.22%
|  |  | Average Active Mode Efficiency: | 83.18%
Sample #1 Does Not Meet The Tier 1 Active Efficiency Standard
Load condition #5: No Load |  |  | AC Input Measurements
|  |  | Measured Input Power | 0.6 | W
Set the Output to No Load |  |  | Measured Input Voltage | 115 | VAC
|  |  | Measured Frequency | 60 | Hz
True Power Factor
|  |  | Total Harmonic Distortion (THD) |  | %
Sample #1 Meets The Tier 1 No Load Standard

## Sample #2
Sample #2 Test Results - 115 VAC / 60 Hz
Output Measurements |  |  | AC Input Measurements
Load Condition #1: 100%
Set Output Current to | 5000 | mA | Measured Input Power |  | W
Min Output Current | 4900 | mA | Measured Input Voltage | 115 | VAC
Max Output Current | 5100 | mA | Measured Frequency | 60 | Hz
True Power Factor
Measured Output Current | 5000 | mA | Total Harmonic Distortion (THD) |  | %
Measured Output Voltage |  | V | Calculated Power Consumed |  | W
Calculated Output Power |  | W | Calculated Efficiency (Ouput/Input)
Enter Output and Input Measurments
Load Condition #2: 75%
Set Output Current to | 3750 | mA | Measured Input Power |  | W
Min Output Current | 3650 | mA | Measured Input Voltage | 115 | VAC
Max Output Current | 3850 | mA | Measured Frequency | 60 | Hz
True Power Factor
Measured Output Current | 3750 | mA | Total Harmonic Distortion (THD) |  | %
Measured Output Voltage |  | V | Calculated Power Consumed |  | W
Calculated Output Power |  | W | Calculated Efficiency (Ouput/Input)
Enter Output and Input Measurments
Load Condition #3: 50%
Set Output Current to | 2500 | mA | Measured Input Power |  | W
Min Output Current | 2400 | mA | Measured Input Voltage | 115 | VAC
Max Output Current | 2600 | mA | Measured Frequency | 60 | Hz
True Power Factor
Measured Output Current | 2500 | mA | Total Harmonic Distortion (THD) |  | %
Measured Output Voltage |  | V | Calculated Power Consumed |  | W
Calculated Output Power |  | W | Calculated Efficiency (Ouput/Input)
Enter Output and Input Measurments
Load Condition #4: 25%
Set Output Current to | 1250 | mA | Measured Input Power |  | W
Min Output Current | 1150 | mA | Measured Input Voltage | 115 | VAC
Max Output Current | 1350 | mA | Measured Frequency | 60 | Hz
True Power Factor
Measured Output Current | 1250 | mA | Total Harmonic Distortion (THD) |  | %
Measured Output Voltage |  | V | Calculated Power Consumed |  | W
Calculated Output Power |  | W | Calculated Efficiency (Ouput/Input)
Enter Output and Input Measurments
Average Active Mode Efficiency:
Load condition #5: No Load |  |  | AC Input Measurements
|  |  | Measured Input Power |  | W
Set the Output to No Load |  |  | Measured Input Voltage | 115 | VAC
|  |  | Measured Frequency | 60 | Hz
True Power Factor
|  |  | Total Harmonic Distortion (THD) |  | %

## Sample #3
Sample #3 Test Results - 115 VAC / 60 Hz
Output Measurements |  |  | AC Input Measurements
Load Condition #1: 100%
Set Output Current to | 5000 | mA | Measured Input Power | W
Min Output Current | 4900 | mA | Measured Input Voltage | VAC
Max Output Current | 5100 | mA | Measured Frequency | Hz
True Power Factor
Measured Output Current |  | mA | Total Harmonic Distortion (THD) | %
Measured Output Voltage |  | V | Calculated Power Consumed | W
Calculated Output Power |  | W | Calculated Efficiency (Ouput/Input)
Enter Output and Input Measurments
Load Condition #2: 75%
Set Output Current to | 3750 | mA | Measured Input Power | W
Min Output Current | 3650 | mA | Measured Input Voltage | VAC
Max Output Current | 3850 | mA | Measured Frequency | Hz
True Power Factor
Measured Output Current |  | mA | Total Harmonic Distortion (THD) | %
Measured Output Voltage |  | V | Calculated Power Consumed | W
Calculated Output Power |  | W | Calculated Efficiency (Ouput/Input)
Enter Output and Input Measurments
Load Condition #3: 50%
Set Output Current to | 2500 | mA | Measured Input Power | W
Min Output Current | 2400 | mA | Measured Input Voltage | VAC
Max Output Current | 2600 | mA | Measured Frequency | Hz
True Power Factor
Measured Output Current |  | mA | Total Harmonic Distortion (THD) | %
Measured Output Voltage |  | V | Calculated Power Consumed | W
Calculated Output Power |  | W | Calculated Efficiency (Ouput/Input)
Enter Output and Input Measurments
Load Condition #4: 25%
Set Output Current to | 1250 | mA | Measured Input Power | W
Min Output Current | 1150 | mA | Measured Input Voltage | VAC
Max Output Current | 1350 | mA | Measured Frequency | Hz
True Power Factor
Measured Output Current |  | mA | Total Harmonic Distortion (THD) | %
Measured Output Voltage |  | V | Calculated Power Consumed | W
Calculated Output Power |  | W | Calculated Efficiency (Ouput/Input)
Enter Output and Input Measurments
Average Active Mode Efficiency:
Load condition #5: No Load |  |  | AC Input Measurements
|  |  | Measured Input Power | W
Set the Output to No Load |  |  | Measured Input Voltage | VAC
|  |  | Measured Frequency | Hz
True Power Factor
|  |  | Total Harmonic Distortion (THD) | %

## Nameplate Photo
Insert photo of the Power Supply
nameplate label that will be applied when the product ships.
when the product ships.
Reduce the size of the image to keep
the file size small.